## TBE
CODE STATUS (1)
TECHNICAL BID EVALUATION FOR OILY WATER SEPARATOR | [13 empty] | A : ACCEPTABLE ALTERNATIVE
O : OPTIONAL ( EXTRA COST)
COMPANY : |  |  | BID REFERENCE : | Applicable Specification(s) and corresponding document(s) : |  | GRADING SYSTEM (2) | F = in conformity with requirements | 100 | Comments : |  |  |  |  | Y : STATEMENT ACCEPTED
BUYER : HHI |  |  | PREPARED BY : |  |  |  | A = risky or unclear | 50 | [5 empty] | X : NOT ACCEPTED
TAG N° : SAO-5330501 |  |  | REVISION : 0 |  |  |  | X = disqualifying | 0 | [5 empty] | C : CLARIFCATION REQUIRED
REQUISITION N° : I-RM-3A36.06-5330-667-KES-301 | [6 empty] | Void | ---- | [5 empty] | E : BIDDER TO SUBMIT
NO. | DESCRIPTION OF PROJECT SPECIFICATION |  |  | SPECIFICATION REQUIREMENT | BIDDER'S COMMENT / RESPONSE AS PER SUBMITTED TQS
Detegasa
[10 empty] | TQS reference : | Status (see code 1) | Score (2) | Formula result
1.0 | BID SUBMISSION | [11 empty] | ----
1.1 | Essential Submission Required Document Checking Sheet |  |  | Refer to Appendix 11 in the Requisition | [8 empty] | ----
1.1.1 | - Complete description of the scope of supply |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F
1.1.2 | - Filled-in TBE table |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.3 | - Deviation / Clarification List |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.4 | - Prelminary GAD with weight & dimension |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.5 | - Preliminary Utility List |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.6 | - Preliminary datasheet |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.7 | - Preliminary Sizing Calculation |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.8 | - Preliminary P&ID |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.9 | - E&I technical compliance check sheet |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.10 | - Spare part and Special Tool list |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.11 | - Sub-Vendor List |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.12 | - Fabrication Schedule Bar Chart with proposed delivery |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.13 | - Vendor Document Schedule comment |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
1.1.14 | - Reference List |  |  | Bidder to submit with technical quotation | [5 empty] | YES | Y | F | 100
2.0 | GENERAL SCOPE OF WORK | [11 empty] | ----
2.1 | System and Equipment detail design |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
2.2 | Manufacture, shop assembly, corrosion protection |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
2.3 | Identification, inspection, testing |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
2.4 | Other engineering service including layout drawing, stress analysis, technical data book, drawings, technical meetings, control system interface, vibration and noise data |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
2.5 | Approved vendors list |  |  | As per Project Approved Vendor List, Bidder to confirm | [5 empty] | PARTIALLY COMPLIANCE | Y | A | 50
2.5.1 | - Sub vendor list |  |  | Bidder to submit their sub-contractor list for approval as part of Vendor documentation, Bidder to confirm | [5 empty] | YES | Y | F | 100
2.6 | Required documentation as per Vendor Data Requirements |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
2.6.1 | - Vendor Data to be submitted |  |  | As per MR and I-ET-3A36.06-9000-911-KSL-001-DOCUMENT CONTROL PROCEDURE. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.6.2 | - Final Hadnover Document |  |  | As per Material Requisition. Final dossiers shall be available for final review within 1 month of dispatch of equipment. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.6.3 | - Dispatch of Documents |  |  | As per Material Requisition. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.6.4 | - Inspection Release Certificate |  |  | As per Material Requisition. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.6.5 | - Material Traceability, Marking and Manufacturing Work Traceability |  |  | As per Material Requisition. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.6.6 | - Instruction manuals for operation and maintenance of the equipment/PACKAGE shall be provided in Portuguese language. |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.7 | Complete liaison work with sub suppliers & sub vendors |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.8 | Performance Guarantee & Mechanical Warranty |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
2.9 | 3D modeling (PDMS convertible, such as step file), native files (STEP/STP) |  |  | 1) for 30% review, 2) for 60% review, 3) for 90% review. Final as built model. Bidder to confirm | [5 empty] | YES | Y | F | 100
2.10 | Submission of Native files (AutoCAD) of detailed drawings |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
2.11 | Preservation / Packing suitable for seaworthy and marine climate |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES, ACCORDING TO THE DISCUSSION IN THE TC AND DEVIATION LIST SHEETS | Y | A | 50
2.12 | Kick Off Meeting at BUYER’s Office (1 time, 2 working days) |  |  | Bidder to confirm | [5 empty] | YES, BY VIDEOCALL DUE TO PANDEMIC RESTRICTIONS | Y | A | 50
2.13 | Pre-Inspection Meeting at Bidder’s Premise (1 working day) |  |  | Bidder to confirm | [5 empty] | YES, AT DETEGASA PREMISES | Y | F | 100
2.14 | HAZOP Meeting at BUYER’s Office (1 time, 2 working days) |  |  | Bidder to confirm | [5 empty] | Accoring to the latest discussion, this is not applicable for our package | Y | F | 100
2.15 | Technical Clarification Meeting at BUYER’s Office (2 times, 2 working days each) |  |  | Bidder to confirm | [5 empty] | YES, BY VIDEOCALL DUE TO PANDEMIC RESTRICTIONS | Y | A | 50
2.16 | Technical Clarification Meeting at BIDDER’s Premises or Conference Call (anytime when required) |  |  | Bidder to confirm | [5 empty] | YES, BY VIDEOCALL DUE TO PANDEMIC RESTRICTIONS | Y | A | 50
2.17 | Material Identification & Traceability, Welding, Inspection |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
2.18 | SHIPPED LOOSE ITEM control |  |  | As per Material Requisition. Bidder to confirm. | [5 empty] | YES | Y | F | 100
2.19 | Third Party Certified Spreader Beam (along with shackles, slings) suitable for single point lift for each skid. |  |  | Required. Bidder to confirm. | [5 empty] | NOT INCLUDED IN OUR SCOPE OF SUPPLY | Y | F | 100
2.2 | Supervision service for installation, pre/commissioning & start-up |  |  | Required dates’ amount and lump sum pricing with daily rates shall be proposed by Bidder. | [5 empty] | YES | Y | F | 100
2.21 | Punch Close |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
2.22 | Nameplates and tag plates as per project requirements. |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
2.22.1 | - Equipment shall have nameplates in Brazilian Portuguese language, made of stainless steel AISI 316L, with 3 mm minimum thickness and fixed by stainless steel (AISI 316L) bolts or fasteners on visible and accessible location |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
2.23 | First fill of lubricant and other consumables |  |  | as required for FAT Package equipment shall be specified and procured with recommended lubricants | [5 empty] | YES | Y | F | 100
2.24 | Special tools and spare parts |  |  | Required as per MR. | [5 empty] | YES | Y | F | 100
2.24.1 | - Special Tools and equipment required for installation, operation and maintenance, if any |  |  | Required | [5 empty] | YES | Y | F | 100
2.24.2 | - Spare parts for Start-up and commissioning |  |  | Bidder to provide | [5 empty] | YES | Y | F | 100
2.24.3 | - List of 2-year operational spare parts (Priced list) |  |  | Bidder to submit | [5 empty] | YES | Y | F | 100
2.24.4 | - List of Capital spares (Priced list) |  |  | Bidder to submit | [5 empty] | IN A LATER STAGE, IN CASE OF ORDER | Y | F | 100
2.25 | Warning signs in Brazilian Portuguese language shall be provided where risk of personnel injury exist. |  |  | Bidder to provide | [5 empty] | YES | Y | F | 100
2.26 | Training |  |  | Bidder to provide as per Section 10 in I-ET-3010.1M-5330-667-P4X-001. | [5 empty] | YES | Y | F | 100
3.0 | DETAILED SCOPE OF SUPPLY
3.1 | Oily Water Separator Package |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES | Y | F | 100
3.1.1 | One(1) Completed Package is intended to perform the bilge water suction from the Engine Room Bilge Water Settling Tank, with a flow rate of 5 m³/h with the maximum oil content of 500 ppm, and discharge this bilge water flow rate to sea overboard with a maximum oil content of 15 ppm, attending IMO MEPC 107 (49) requirements and Marpol Annex I – Reg. 21. |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.2 | Bilge water oil monitoring system - One(1) sampling collecting point in the Oil Water Separator overboard discharge; - One(1) oil cell with range between 0 and 30 ppm of oil; |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.3 | Control Panel (PN-SAO-5336501) |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.4 | Automation as per Package Classification “P1” as defined in I-ET-3010.00-1200-800-P4X-002(AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS) and I-ET-3010.1M-1200-800-P4X-014(AUTOMATION INTERFACE OF PACKAGE UNITS PACKAGE INTERFACE) |  |  | Required | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
3.1.5 | All required sub-equipment and/or componets in the Package based on PACKAGER’s proposed technology. |  |  | Bidder to advise on detail of proposed technology and list of required sub-equipment and/or componets | [5 empty] | YES | Y | F | 100
3.1.6 | All required valves, PSV and piping |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.7 | Junction boxes and control panels, as required; |  |  | Required | [5 empty] | YES | Y | F
3.1.8 | Drain collector connected to the drain system of the unit; |  |  | Required | [5 empty] | YES | Y | F
3.1.9 | Complete one(1) common skid assembly with resilient mounting for Oily Water Separator Package. - HHI standard type 4, specified in 5.2.3 Equipment support type selection - Self-supporting structural skid with drip pan, grating for access ways etc. along with earthing (grounding) / bonding. |  |  | Required | [5 empty] | YES, ALTHOUGH GRATING IS NOT NECESSARY, DUE TO THE DIMENSIONS AND CONFIGURATION OF THE PACKAGE | Y | A
3.1.10 | On-skid access platforms and ladders, including ladder and stairway to upper levels for any skids with multiple levels as applicable – Requirement in Brazil Regulation NR 12 shall be complied with. |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.11 | Access steps/platforms or ladders to be mounted outside of the skid edge shall be provided with fixing brackets and bolts/nuts as shipped loose. Mounting pads for the fixing bolts shall be welded at the skid edge. |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.12 | All on-skid piping and tubing system including valve and supports terminating in flanged connections at skid edge. (All shipped loose piping spools and valves (if any) shall be completely welded and tested.) |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.13 | All on-skid electrical equipment required for the safe, automatic, continuous operation and monitoring of the package including cable trays/supports for BIDDER and BUYER cables and earthing (grounding) within the package. |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.14 | All on-skid instrumentation and controls required for the safe, automatic, continuous operation and monitoring of the package, including cabling, cable trays and junction boxes supplied via the platform control system BIDDER in accordance with the approved vendor list. Refer to APPENDIX 14 E&I TIE-IN DOCUMENT GUIDANCE TO BIDDERS and provide required interface documents as per the guidance. |  |  | Required | [5 empty] | PARTIALLY COMPLIANCE | Y | A | 50
3.1.15 | Pre-Inspection Meeting(PIM), Material Identification & Traceability, PMI reports, Welding, Inspection, NDT, Heat Treatment as required and Hydrostatic Testing, Bolt tightening Record, Leak Test, Mechanical Completion(MC), Factory Acceptance Test, Punch Close, Final Inspection, Packing & Preservation and Inspection Release Certificate(IRC) |  |  | Required | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | A | 50
3.1.16 | Calculation Reports – for system, capacity, selection and etc. |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.17 | Classification Society Certification (Classification & Certification) |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.18 | Bidder shall issue an authorization to Classification Society allowing direct and full access of COMPANY(Petrobras)/HHI to all information regarding certification of project and fabrication of equipment and materials. |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.19 | INMETRO compliance Certification |  |  | Required | [5 empty] | NO, WE UNDERSTAND IT IS NOT APPLICABLE FOR OUR PACKAGE | Y | F | 100
3.1.20 | Surface preparation and painting based on I-ET-3010.00-1200-956-P4X-002 – (PETROBRAS – General Painting Technical Specification). |  |  | Required | [5 empty] | YES, ACCORDING TO THE DISCUSSION IN THE TC AND DEVIATION LIST SHEETS | Y | A | 50
3.1.21 | Tagging and Nameplates (dual language: English and Portuguese, respectively) for Package / Equipment / Component |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.22 | Safety sign per specification I-ET-3010.00-5400-947-P4X-002 |  |  | Required | [5 empty] | YES | Y | F | 100
3.1.23 | Transport restraints, lifting spreader bars or frames for transportation and installation, complete with slings and shackles, materials, welding and NDE certification and proof load test certification. |  |  | Required | [5 empty] | NOT INCLUDED IN OUR SCOPE OF SUPPLY | Y | F | 100
3.1.24 | Welding and Welding Inspection |  |  | As per per I-ET-3010.00-1200-955-P4X-001, I-ET-3010.00-1200-955-P4X-002 and I-ET-3010.00-0000-970-P4X-001. | [5 empty] | ACCORDING TO OUR STANDARDS | Y | A | 50
3.1.25 | Non Destructive Testing (NDT) |  |  | As per I-ET-3010.00-1000-970-P4X-002 | [5 empty] | ACCORDING TO OUR STANDARDS | Y | A | 50
3.1.26 | Bolted joints asembly and management |  |  | As per I-ET-3010.00-1200-200-P4X-116 | [5 empty] | ACCORDING TO OUR STANDARDS | Y | A | 50
4 | TECHNICAL REQUIREMENT
4.1 | General | [11 empty] | ----
4.1.1 | Area Classification |  |  | Non classified compartment | [5 empty] | YES | Y | F | 100
4.1.1 | Equipment Location |  |  | Engine Room as per I-DE-3010.1M-1350-942-P4X-001, Engine Room Layout | [5 empty] | YES | Y | F | 100
4.1.2 | Design Life |  |  | 30-year life in a corrosive offshore environment | [5 empty] | YES | Y | F | 100
4.1.3 | Environment Conditions |  |  | As specified in Datasheet(I-FD-3010.1M-5133-661-P4X-001), MOTION ANALYSIS( I-RL-3010.1M-1350-960-P4X-009) and METOCEAN DATA(I-ET-3A36.00-1000-941-PPC-001). | [5 empty] | YES | Y | F | 100
4.1.4 | Motion & Acceleration |  |  | As per I-ET-3A36.00-1000-941-PPC-001 METOCEAN DATA and I-RL-3010.1M-1350-960-P4X-009 MOTION ANALYSIS | [5 empty] | YES | Y | F | 100
4.1.5 | Utility Consumption incl. Eletric Power Consumption |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
4.2 | Design Conditions (at Bilge Water Settling Tank, TQ-5330501)
4.2.1 | DESIGN TEMPERATURE , °C |  |  | 60 | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A | 50
4.2.2 | PRESSURE , BARG |  |  | 3.4 | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A | 50
4.3 | Operating Conditions (at Bilge Water Settling Tank, TQ-5330501) | [11 empty] | ----
4.3.1 | OPERATING TEMPERATURE , °C |  |  | 30 | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A | 50
4.3.2 | PRESSURE , BARG |  |  | ATM | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A | 50
4.4 | Capacity |  |  | 5 m³/h | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A
4.5 | Maximum remaining oil content |  |  | 15 ppm | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A | 50
4.6 | Utility Requirement |  |  | as per I-RL-3010.1M-1200-940-P4X-001 GENERAL SPECIFICATION FOR AVAILABLE UTILITIES | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A | 50
4.7 | Electrical Power Supply |  |  | as per I-ET-3010.00-5140-700-P4X-003 ELEC REQUIREMENTS FOR PKG FOR OFFSHORE UNITS | [5 empty] | SHIPYARD´S SCOPE OF SUPPLY Noted and confirmed | Y | A | 50
4.8 | Separator | [11 empty] | ----
4.8.1 | Type / Model |  |  | Bidder to confirm | [5 empty] | DELTA OWSAN-5 | Y | F | 100
4.8.2 | Q'ty / Configuration |  |  | Bidder to confirm | [5 empty] | 1 | Y | F | 100
4.8.3 | Design Code |  |  | Bidder to confirm | [5 empty] | ASME (Tanks) | Y | F | 100
4.8.4 | Material |  |  | Bidder to confirm | [5 empty] | ASTM A516 Grade 60 (Tanks) | Y | F | 100
4.9 | Pump - 1 | [11 empty] | ----
4.9.1 | Service / Purpose |  |  | Bidder to confirm | [5 empty] | Process pump | Y | F | 100
4.9.2 | Design Code |  |  | Bidder to confirm | [5 empty] | Generally API 676 | Y | F | 100
4.9.3 | Type |  |  | Bidder to confirm | [5 empty] | Positive displacement pump (Screw type) | Y | F
4.9.4 | Rated power |  |  | Bidder to confirm | [5 empty] | 3,6 kW | Y | F | 100
4.9.5 | Flow rate |  |  | Bidder to confirm | [5 empty] | Max. 6 m3/h | Y | F | 100
4.9.6 | IP grade |  |  | Bidder to confirm | [5 empty] | IP 54 | Y | F | 100
4.9.7 | PSV |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
4.9.8 | Material |  |  | Bidder to confirm | [5 empty] | Stainless Steel | Y | F | 100
4.9.9 | Test |  |  | Bidder to confirm | [5 empty] | NOT APPLICABLE | A | C | ----
4.9.10 | Electric motor |  |  | as per I-ET-3010.00-5140-712-P4X-001 | [5 empty] | YES, ACCORDING TO THE DISCUSSION IN THE TC AND DEVIATION LIST SHEETS | Y | A | 50
4.10 | Pump - 2 (Air operated sludge pump) | [11 empty] | ----
4.10.1 | Service / Purpose |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F
4.10.2 | Design Code |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F | 100
4.10.3 | Type |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F
4.10.4 | Rated power |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F | 100
4.10.5 | Flow rate |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F | 100
4.10.6 | IP grade |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F | 100
4.10.7 | PSV |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F | 100
4.10.8 | Material |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F | 100
4.10.9 | Test |  |  | Bidder to confirm | [5 empty] | Not Applicable | Y | F | 100
4.10.10 | Electric motor |  |  | as per I-ET-3010.00-5140-712-P4X-001 | [5 empty] | Not Applicable | Y | F | 100
4.12 | Monitoring System | [11 empty] | ----
4.12.1 | Configuration |  |  | - One(1) sampling collecting point in the Oil Water Separator overboard discharge; - One(1) oil cell with range between 0 and 30 ppm of oil; | [5 empty] | YES | Y | F | 100
4.12.2 | Detector Model |  |  | Bidder to advise | [5 empty] | DOM-107 | Y | A | 50
4.13 | Filter (if required in proposed solution) | [11 empty] | ----
4.13.1 | Service / Purpose |  |  | Bidder to confirm | [5 empty] | ABSORPTION TANK | Y | F | 100
4.13.2 | Filter Type |  |  | Bidder to confirm | [5 empty] | ABSORPTION FILTER | Y | F | 100
4.13.3 | Design Code |  |  | Bidder to confirm | [5 empty] | ASME (TANK) | Y | F | 100
4.13.4 | Material |  |  | Bidder to confirm | [5 empty] | MODIFIED CELLULOSE (FILTER) ASTM A516 Grade 60 (TANK) | Y | F | 100
4.13.5 | Coating(Internal/External) |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.13.6 | Operating / design temperature |  |  | Bidder to confirm | [5 empty] | Max. 50ºC | Y | F | 100
4.13.7 | Operating / design pressure |  |  | Bidder to confirm | [5 empty] | 2,5 BAR | Y | F | 100
4.13.8 | Filtration Efficiency |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.13.9 | Dimensions |  |  | Bidder to confirm | [5 empty] | SEE PRELIMINARY DRAWINGS | Y | F | 100
4.13.10 | Volume |  |  | Bidder to confirm | [5 empty] | SEE PRELIMINARY DRAWINGS | Y | F | 100
4.13.11 | Internals |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.13.12 | Instruments attached on Filter |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.14 | Tank | [11 empty] | ----
4.14.1 | Service / Purpose |  |  | Bidder to confirm | [5 empty] | GRAVITY SEPARATION | Y | F | 100
4.14.2 | Design Code |  |  | Bidder to confirm | [5 empty] | ASME (TANK) | Y | F | 100
4.14.3 | Material |  |  | Bidder to confirm | [5 empty] | ASTM A516 Grade 60 | Y | F | 100
4.14.4 | Coating(Internal/External) |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.14.5 | Operating / design temperature |  |  | Bidder to confirm | [5 empty] | MAX. 60 ºc | Y | F | 100
4.14.6 | Operating / design pressure |  |  | Bidder to confirm | [5 empty] | 1,5 bar | Y | F | 100
4.14.7 | Dimensions |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.14.8 | Volume |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.14.9 | Internals |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.14.10 | Instruments attached on Tank |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.15 | Heater (Electrical Heater) | [11 empty] | ----
4.15.1 | Service / Purpose |  |  | Bidder to confirm | [5 empty] | HEATING OF OIL IN THE GRAVITY SEPARATION TANK | Y | F | 100
4.15.2 | Design Code |  |  | Bidder to confirm | [5 empty] | N/A | Y | F | 100
4.15.3 | Design Duty | , kW |  | Bidder to confirm | [5 empty] | 1,5 kW | Y | F | 100
4.15.4 | Heater Maker / Model No. |  |  | Bidder to confirm | [5 empty] | ELECTRIFOR or similar | Y | F | 100
4.15.5 | Material |  |  | Bidder to confirm | [5 empty] | SS316L | Y | F | 100
4.15.6 | Coating(Internal/External) |  |  | Bidder to confirm | [5 empty] | N/A | Y | F | 100
4.15.7 | Operating / design temperature |  |  | Bidder to confirm | [5 empty] | 45 ºC | Y | F | 100
4.15.8 | Operating / design pressure |  |  | Bidder to confirm | [5 empty] | 3 bar | Y | F | 100
4.15.9 | Dimensions |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.15.10 | Volume |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.15.11 | Internals |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.15.12 | Instruments attached on Heater |  |  | Bidder to confirm | [5 empty] | SEE TECHNICAL SPECIFICATION | Y | F | 100
4.16 | PIPING | [11 empty] | ----
4.16.1 | Reference Specification |  |  | I-ET-3010.1M-1200-200-P4X-002 (PIPING SPECIFICATION FOR HULL) | [5 empty] | Accoding to our standards | Y | A | 50
4.16.2 | Material for piping |  |  | B14H | [5 empty] | SS316L | Y | A | 50
4.16.3 | Valves |  |  | As per I-ET-3010.1M-1200-200-P4X-002 (PIPING SPECIFICATION FOR HULL) | [5 empty] | Accoding to our standards | Y | A | 50
4.16.4 | Bolting in piping |  |  | As per I-ET-3010.00-1200-251-P4X-001(REQUIREMENTS FOR BOLT MATERIALS) and I-ET-3010.1M-1200-200-P4X-002 (PIPING SPECIFICATION FOR HULL) | [5 empty] | Accoding to our standards | Y | A | 50
4.17 | Electrical and Instrument | [11 empty] | ----
4.17.1 | E&I technical compliance check sheet |  |  | Bidder to complete check sheet in Appendix 14, No.5 | [5 empty] | YES | Y | F | 100
4.17.2 | I-ET-3010.00-5140-700-P4X-003 (ELECTRICAL REQUIREMENTS FOR PACKAGES FOR OFFSHORE UNITS) |  |  | Bidder to confirm | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
4.17.3 | I-ET-3010.00-5140-700-P4X-001 (SPECIFICATION FOR ELECTRICAL DESIGN FOR OFFSHORE UNITS) |  |  | Bidder to confirm | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
4.17.4 | I-ET-3010.00-1200-800-P4X-002 (AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS) |  |  | Bidder to confirm | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
4.17.5 | I-ET-3010.00-1200-800-P4X-013 (GENERAL CRITERIA FOR INSTRUMENTATION PROJECTS) |  |  | Bidder to confirm | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
4.17.6 | Package Control Type |  |  | P1 as per I-ET-3010.00-1200-800-P4X-002_AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS | [5 empty] | YES | Y | F | 100
4.17.7 | Oil Water Separator Control Panel(PN-SAO-5336501) |  |  | Required as per I-ET-3010.00-5520-888-P4X-001(AUTOMATION PANELS) | [5 empty] | YES, ACCORDING TO THE DISCUSSION IN THE TC AND DEVIATION LIST SHEETS | Y | A | 50
4.17.8 | HMI |  |  | Bidder to confirm as per I-ET-3010.00-1200-800-P4X-002(AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS) | [5 empty] | YES, ACCORDING TO THE DISCUSSION IN THE TC AND DEVIATION LIST SHEETS | Y | A | 50
4.17.9 | Signal Interface |  |  | As per I-ET-3010.00-1200-800-P4X-002 (AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS and I-DE-3010.1M-5330-944-P4X-001(P&ID for BILGE, SLUDGE, BALLAST (AFT) AND GENERAL SERVICE SEAWATER SYSTEM) | [5 empty] | YES, ACCORDING TO THE DISCUSSION IN THE TC AND DEVIATION LIST SHEETS | Y | A | 50
4.17.10 | Type of PLC |  |  | Bidder to confirm | [5 empty] | SIEMENS S7-1200 | Y | F | 100
4.18 | Structure steel and bolt&nut | [11 empty] | ----
4.18.1 | Reference Specification/Code |  |  | Bidder to confirm | [5 empty] | ACCORDING TO OUR STANDARDS | Y | A | 50
4.18.2 | Structure steel grade |  |  | Bidder to confirm | [5 empty] | Carbon steel S275 JR | Y | A | 50
4.18.3 | Bolt and Nut |  |  | As per I-ET-3010.00-1200-251-P4X-001(REQUIREMENTS FOR BOLT MATERIALS) | [5 empty] | YES | Y | F | 100
4.18.4 | Grating |  |  | As per I-ET-3010.00-1352-130-P4X-001 (Floor Gratings, Tray systems and Guardrails made of Composite Materials) | [5 empty] | NOT APPLICABLE, CONSIDERING THE DIMENSIONS AND CONFIGURATION OF OUR PACKAGE | Y | A | 50
4.19 | Noise level , dB(A) |  |  | As per I-ET-3010.1M-1200-300-P4X-002 | [5 empty] | YES | Y | F | 100
4.20 | Vibration |  |  | As per I-ET-3010.1M-1200-300-P4X-002 | [5 empty] | YES, ACCORDING TO OUR STANDARDS | Y | F | 100
4.21 | Size of Overall Skid (L x W x H mm) |  |  | Bidder to confirm | [5 empty] | 2820 x 2120 x 2197 mm | Y | F | 100
4.22 | Weight (Net(kg)/ Operating(kg)) |  |  | Bidder to confirm | [5 empty] | Approx. Net Weight: 2500 kg Approx. Operating weight: 3700 kg Subject to be revised durting project execution | Y | A | 50
5 | INSPECTION AND TESTING | [11 empty] | ----
5.1 | Inspection and Testing of entire package shall be as per approved ITP |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.2 | Third party inspection & Certifying agency |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.3 | Material inspection and certification as per project specification |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.4 | Mechanial running test as per project specification |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.5 | Full load test as per project specification |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.6 | Hydrotest for pump |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.7 | Auxiliary equipment test |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.8 | Complete unit string test as per project specification |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.9 | Noist test |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.1 | Vibration test |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.11 | Instrumentation inspection and testing as per project specification |  |  | Bidder to confirm | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
5.12 | Factory and Onboard Acceptance Tests |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES, ACCORDING TO Section 6 along with Table 1 and Table 2 in EXHIBIT V, as both parties agreed in the Deviation list | Y | F | 100
6 | SURFACE PREPARATION AND COATINGS | [11 empty] | ----
6.1 | Painting code |  |  | As per I-ET-3010.00-1200-956-P4X-002. Bidder to confirm. | [5 empty] | YES, ACCORDING TO THE DISCUSSION IN THE TC AND DEVIATION LIST SHEETS | Y | A | 50
6.2 | Final Color Coading |  |  | As per DR-ENGP-I-1.15. Bidder to confirm. | [5 empty] | YES | Y | F | 100
7 | SPECIFICATIONS, CODES AND STANDARDS | [11 empty] | ----
7.1 | Industrial Codes and Standards |  |  | Equipment governed by this Specification shall be designed, manufactured and tested in accordance with the latest edition of the following primary Codes and Standards, including any supplementary revisions or addenda, unless modified specifically by Project Specifications listed in the Requisition and this TBE table. | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
7.2 | Package Specifications |  |  | As per Appendix 2 in MR | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
7.3 | Project Specifications |  |  | As per Appendix 3 in MR | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
7.4 | Project Drawings |  |  | As per Appendix 4 in MR | [5 empty] | YES, WITH COMMENTS/DEVIATIONS | Y | A | 50
7.5 | International Code and Standards |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES | Y | A | 50
7.6 | Brazilian Regulation |  |  | As per I-ET-3010.1M-5330-667-P4X-001 and MR. Bidder to confirm. | [5 empty] | YES | Y | A | 50
8 | GENERAL | [11 empty] | ----
8.1 | Country of origin |  |  | Bidder to confirm | [5 empty] | SPAIN | Y | F | 100
8.2 | Fabrication shop location |  |  | Bidder to confirm | [5 empty] | SPAIN | Y | F | 100
8.3 | Delivery Duration |  |  | Bidder to confirm | [5 empty] | SEVEN (7) MONTHS EXWORKS | Y | F | 100
8.4 | Transportation method |  |  | Bidder to confirm | [5 empty] | SEA FREIGHT | Y | F | 100
8.5 | Reference list of similar installations |  |  | Bidder to confirm | [5 empty] | YES | Y | F | 100
8.6 | Packing list management |  |  | Packing list shall indicate component tag(project numbering) or part number with drawing number(project numbering) | [5 empty] | YES | Y | F | 100
----
|  |  |  | PASS (P) OR FAIL (F) if any 0 scoring | [5 empty] | P
|  |  |  | TENDERER TECHNICAL TOTAL SCORING | [5 empty] | 16800
|  |  |  | RECOMMENDATION | [5 empty] | Detegasa is technically acceptable

## Sheet1 (hidden)
8.6
8.7
8.8 |  | Painting
Protective Coating & Linning
8.9
8.1
By Vendor
9
10 |  | Shop Inspection & Test
- Inspection and test at shop for equipment
- Inspection ans test at shop for Instrument, including
function test at shop
11.0 |  | Documentation :
|  | Documents + Drawing submission |  |  |  |  | As per VDRL of Doc. BRA- RQ- M-004
Rev Q1
12.0 | SKID MODULE SIZE AND WEIGHT
Glycol Regeneration Skid
- Size
|  |  |  | First Level | 12m x 6 m
|  |  |  | Second Level | 6m x 6m
|  |  |  | Total Height | 9 m
|  |  |  | - Weight | By Vendor
13 | SITE SUPERVISION |  |  |  | Required
14 | TRAINING |  |  |  | Required
15 | ACCEPTANCE CRITERIA |  |  |  | As per Cl. 6.8. Of Doc
BRA- RQ-M-004 Rev Q1