## Index
I N D E X
1. General Remarks and References
2. Description
3. Load List for P-78

## General Remarks and References
GENERAL REMARKS AND REFERENCES
1.GENERAL REMARKS
(1) Electrical Load List is in line with Single Line Diagram and Electrical Equipment Calculation Documents.
(2) Efficiency factors for consumers are considered in load list, whereas efficiency factors of transformers are considered in transformer sizing calculation.
2.REFERENCES
(1) I-LI-3010.1M-5265-773-P4X-001: EMERGENCY LOADS LIST
(2) I-MC-3010.1M-5147-700-P4X-003: ELECTRICAL SYSTEM LOAD BALANCE
(3) I-ET-3010.00-5140-700-P4X-003: ELECTRICAL REQUIREMENTS FOR PACKAGES FOR OFFSHORE UNITS
(4) I-ET-3010.1M-1200-800-P4X-014: AUTOMATION INTERFACE OF PACKAGE UNITS
(5) I-ET-3010.00-1200-800-P4X-002: AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS
3.COLOR LEGEND OF SWITCHGEAR, MCC, DISTRIBUTION BOARD
DESCRIPTION | COLOR | RGB CODE
13.8kV TRANSFORMER |  | R255,G153,B153
6.6kV SWGR |  | R102,G204,B255
480V SWGR & MCC, 480V SWGR |  | R255,G255,B153
480V MCC |  | R153,G255,B204
DC UPS, DC POWER DIST. PANEL |  | R204,G153,B255
AC UPS, AC POWER DIST. PANEL |  | R153,G255,B153
MAIN DIST. BOARD |  | R191,G191,B191
SUB DIST. BOARD |  | R204,G255,B204

## Description
Electrical Load List (Description)
Project Name : Shuqaiq Steam Power Plant | Project Name : Shuqaiq Steam Power Plant
SCHEMATIC TYPE | TAG NO. | EQUIPMENT DESCRIPTION | LOAD TYPE | LOAD RATING |  | NAME PLATE RATED POWER (kW) | PHASE | FULL LOAD AMPS. | VOLT. | EFF. | PF. | Load FACTOR | DUTY FATOR | INPUT |  |  | OPERATION MODE |  |  | MOTOR SPACE HEATER (kW) | NORMAL ESSENTIAL EMERGENCY | Pkg Type (P0/P1/P2/P2S) | Package No | Package Name | Function Unit (EA01/02/03/04) | Maker | REV. No. | Remark
|  |  |  | SHAFT POWER (kW) | kVA | [8 empty] | kW | kVAR | kVA | C | I | S
0 | 1 | 2 | 3 | 4 (P1) | 5 (S1) | 6 (P2) | 7 | 8 (I1) | 9 (V1) | 10 (η) | 11 (COS Φ) | 12 (K1) | 13 (K2) | 14 (P3) | 15 (Q3) | 16 (S3) | 17 (K2) |  |  | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
|  | Column 0 - SCHEMATIC TYPE OF MV SWGR, LV SWGR, MCC FOR LOAD <Input Value> | [6 empty] | < Required Load Input Power (Column 14,15,16) >
|  | Column 1 - Equipment Tag Number <Input Value> | [6 empty] | Column 14 - kW : {(Shaft Power in Column4) ÷ (Eff in Column 10)} × (Load Factor in Column 12) x (Duty Factor in Column 13)
|  | Column 2 - Equipment Description <Input Value> | [6 empty] | ▶ P3 = (P1 ÷ η) × K1 x K2 <Calculated Value>
|  | Column 3 - Equipment Type <Input Value> | [6 empty] | Column 15 - kVAR : kW × TAN Φ
|  | <Normal> | <Emergency Shut-Down> | [5 empty] | ▶ Q3 = P3 × TAN{ARC COS(COS Φ)} <Calculated Value>
|  | M : Motor | M2 : Motor | [5 empty] | Column 16 - kVA : √{(kW)²+(kVAR)²}
|  | N : Non-motor | N2 : Non-motor | [5 empty] | ▶ S3 = √(P3²+Q3²) <Calculated Value>
|  | V : Valve | V2 : Valve | [5 empty] | Column 17 : Load Operation Mode <Input Value>
|  | PL : Panel | PL2 : PANEL | [6 empty] | C : Continuous Load |  |  |  | I : Intermittent Load |  |  | S : Stand-by Load
|  | TR : TRANSFORMER | TR2 : TRANSFORMER | [5 empty] | Column 18 : Rated Power(kW) of Space Heater for Motor <Input Value>
< LOAD RATING (Column 4,5) >
|  | Column 4 - Shaft Power(kW) : Shaft Rated Power of the rotating machine <Input Value> | [6 empty] | Column 19 : Type of Load <Input Value>
|  | Column 5 - kVA : Shaft Power / PF | [7 empty] | ESSENTIAL LOAD : Essential Loads are those loads that shall remain energized by
|  | ▶ S1 = P1 ÷ COS Φ <Calculated Value> | [7 empty] | Emergency Generation System during shutdown stop ESD3-T and during Main Generation
|  | Column 6 - Nameplate Rated Power in kW <Input Value> | [7 empty] | Emergency Load : Emergency Loads are those loads which shall remain energized by batteries (DC or AC UPS)
|  | ※The Nameplate Rated Power of Motor Shall be refer as I-ET-3010.00-5140-712-P4X-001 | [7 empty] | during Emergency, Main, Hull and Auxiliary Generation Systems failure or shutdown.
|  | (LOW-VOLTAGE INDUCTION MOTORS FOR OFFSHORE UNITS) Clause 3.2.1 | [7 empty] | Normal Load : Normal Loads are the loads neither classified as Emergency Loads nor as Essential Loads.
|  | Column 7 - Phase of Equipment <Input Value> | [6 empty] | Column 20 - PKG Type : Refer to Document I-ET-3010.00-5140-700-P4X-003 <Input Value>
|  | Column 8 - Full Load Rated Current in A | [6 empty] | Column 21~22 - PKG TAG NO/ PKG NAME <Input Value>
|  | For 3 Ph ▶ I1 = P2 ÷ η ÷ COS Φ ÷ √3 ÷ V1 × 1000 <Calculated Value> | [6 empty] | Column 23 - PKG Classification : Refer to Document I-ET-3010.1M-1200-800-P4X-014<Input Value>
|  | For 1 Ph ▶ I1 = P2 ÷ η ÷ COS Φ ÷ V1 × 1000 <Calculated Value> | [6 empty] | Column 24 - Maker Name <Input Value>
|  | Column 9 - Rated Voltage in V <Input Value> | [6 empty] | Column 25 - History of Revision <Input Value>
|  | Column 10 - Rated Load Efficiency in decimal <Input Value> | [6 empty] | Column 26 : For Remark <Input Value>
Column 11 - Rated Power Factor in decimal <Input Value>
Column 12 - Load Factor <Input Value>
Column 12 - Duty Factor <Input Value>

## P-78
ELECTRICAL LOAD LIST
Project Name : Petrobas 78 FPSO
Outg oing CB AT(AF) | N-M Load Pnl INCB AT | FEEDER NO. | SCHEMATIC TYPE | TAG NO. | EQUIPMENT DESCRIPTION | LOAD TYPE | LOAD RATING |  | NAME PLATE RATED POWER (kW) | PHASE | FULL LOAD AMPS. | VOLT. | EFF. | PF. | Load Factor | DUTY FACTOR | INPUT |  |  | OPERATION MODE |  |  | MOTOR SPACE HEATER (kW) | NORMAL ESSENTIAL EMERGENCY | Pkg Type (P0/P1/P2/P2S) | Package No | Package Name | Function Unit (EA01/02/03/04) | MAKER | REV. No. | Remark
|  |  |  | Unit-1 |  |  | SHAFT POWER (kW) | kVA | [8 empty] | kW | kVAR | kVA | C | I | S
FOR EXAMPLE
|  |  |  | M-UH-5139502A-01A | Hydraulic Power Unit Motor for Submerged Pumps - Main Motor | M | 881.82 | 1025.3721 | 970 | 3 | 103.5323 | 6600 | 0.953 | 0.86 | 0.85 | 1 | 786.5131 | 466.6895 | 914.5501 | ㅇ |  |  |  | NORMAL | P2S | PN-5143510A | HYDRAULIC POWER UNIT FOR SUBMERGED PUMPS | EA04