## Tray Segregation
P78 FPSO Project - Cable Tray Segregation Table - Hull & LQ
Tray System |  | MV (6.6kV) | LV Normal (440V/220V/120V) | LV Essential & Emergency (440V/220V/120V) | Inst Non-IS (instrumentation, automation and control) | Inst IS (intrinsically safe circuits) | Safety Non-IS | Safety IS | Telecom PAGA A | Telecom PAGA B | Communication network cables (any kind)
|  | MT | LT | ET | NT | IT | FNT | FIT | PA | PB | DT
MV (6.6kV) | MT | 0 |  |  | 750 | 750 | 750 | 750 | 750 | 750 | 750
LV Normal (440V/220V/120V) | LT |  | 0 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300
LV Essential & Emergency (440V/220V/120V) | ET |  |  | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Inst Non-IS (instrumentation, automation and control) | NT | MT: 750; LT: 300; ET: 300; NT: 0
Inst IS (intrinsically safe circuits) | IT | MT: 750; LT: 300; ET: 300; IT: 0
Safety Non-IS | FNT | MT: 750; LT: 300; ET: 300; FNT: 0
Safety IS | FIT | MT: 750; LT: 300; ET: 300; FIT: 0
Telecom PAGA A | PA | MT: 750; LT: 300; ET: 300; PA: 0
Telecom PAGA B | PB | MT: 750; LT: 300; ET: 300; PB: 0
Communication network cables (any kind) | DT | MT: 750; LT: 300; ET: 300; DT: 0
** Refer to I-ET-3010.00-5140-700-P4X-001 Specification for Electrical Design for Offshore Unit, Section 3.10.2. The final tray segregation with Buyer's acceptance shall be determined during detail engineering.