## TBE_Process
TECHNICAL CLARIFICATION SHEET FOR OILY WATER SEPARATOR
COMPANY : PETROBRAS |  |  |  | BID REFERENCE(TBE No.) : | Applicable Specification(s) and corresponding document(s) : |  | CPY (COMPANY) : PETROBRAS HHI(PURCHASER) : HYUNDAI HEAVY INDUSTRIES CO., LTD BIDDER : Compass | CPY (COMPANY) : PETROBRAS HHI(PURCHASER) : HYUNDAI HEAVY INDUSTRIES CO., LTD BIDDER : Compass | Note 1. : BIDDER'S RESPONSE shall contain clarification and response in each item and any deviation against to the project requirements shall be captured in the APPENDIX 8 DEVIATION EXCEPTION FORM in RFQ. Bidder shall mark the deviation and clarification number for tracking.
PURCHASER : HHI |  |  |  |  | Bidder's Proposal NO : US-100920-SYF
TAG N° : |  |  |  | PREPARED AND CONSOLIDATED BY : | RFQ No. : I-RM-3A36.06-5330-667-HHI-301
REQUISITION N° : |  |  |  | REVISION : 0
NO. | Disc. | Date | CLARIFICATION REQUEST |  | SPECIFICATION REQUIREMENT or REFERENCE DOC/No. | BID Clarificaiton Meeting (13-July-2021) | HHI's Reply | Bidder's Reply | STATUS | REMARK
1 | Process | 2021-07-09 | Maximum Suction Height is 4.5m in Bidder proposal. Purchaser understood additional feed pump is not required when elevation between bilge tank LT2 set and oily water sepator tank bottom is less than 4.5m. Bidder to confirm. The feed water suction availability. |  | OFE47862 rev0 OWSAN-5 TEC page 7 Maximum Suction Height | HHI will provide pressure drop calculation from bilge water settling tank to package tie-in. Detegasa will check and confirm on feed water suction availability based on HHI information for pressure drop. | HHI provided requested information and waiting for Detegasa response. | Proposal was updated accordingly. | Closed
2 | Process | 2021-07-09 | Bidder to ensure package equipment design intergrity based on utility system data indicated in section 8.4 in the I-ET-3010.1M-5330-667-P4X-001_C_SPECIFICATION FOR OILY WATER SEPARATOR PACKAGE (SAO-5330501). |  | OFE47862 rev0 OWSAN-5 TEC page 7 Air Consumption / Flushing Water Consumption | Detegas confirms and comply. Pressure regulator will be considered in scope of supply by Detegas inside skid. Pressure relief valve will also provided at compressed air supply line. For fresh water supply line, pressure relief valve at first oil separator will be protected for package. | Noted and closed |  | Closed
3 | Process | 2021-07-09 | (quote) It is also possible to carry out the cleaning of the coalescent filter manually, selecting “Manual Flushing On” mode in the control panel, which produces flushing water intake and the discharge to the bilge or oily water tank through valve V7. (unquote) It seems that V7 will not used for manual back-flusing because it's a pressure safety valve. V8 should be used for manual back-flusing. Bidder to check. |  | OFE47862 rev0 OWSAN-5 TEC page 14 PROCESS DESCRIPTION | Detegas confirms that V7 will be used during manual flushing mode operation. | Noted and closed |  | Closed
4 | Process | 2021-07-09 | (quote) If for any reason, the sample has hydrocarbon content higher than 15 ppm, the discharge valve to the sea V16 would close and the recirculation to bilges V17 would open. If this situation continues for more than 10 seconds, the equipment would be blocked and stopped automatically. If, on the contrary, the situation is re-established before this period of time, that is, the samples have a content of hydrocarbons lower than 15 ppm, the equipment would automatically change closing V17 recirculating valve and opening V16 overboard valve. (unquote) As per Sec.6.1 in I-ET-3010.1M-5330-667-P4X-001, Automatic stop of the SAO Bilge Water Pump and close of sea valve after the necessary length of time to block hydraulic hammer effect. Intention of requirement is to ensure package protection in case of inadvertent overboard discharge valve close. Bidder to explain how to control/protect package when overboard dhscharge valve close while package is in operation. |  | OFE47862 rev0 OWSAN-5 TEC page 15_7.PROCESS DESCRIPTION page 18_10. ALARMS AND SHUT DOWN | Detegasa advised PSVs in the skid will protect package itself and XV closing signal send to package control panel to stop feed pump in package. Additional Pressure Switch can be considered as alternative option. Deterges to provide optional price for Pressure Switch in next proposal. | Noted and closed |  | Closed
5 | Process | 2021-07-09 | Pump data on page 16(140l/min@2.5bar) and pump curve(less than 20m @ 1500 rpm &140 l/min) on page 20 is not matched.(but, motor rate speed is 1155 rpm on page 21) Pump selection to be check whether selected model is suitable based on required flowrate and discharge pressure. Bidder to confirm dischage pressure @ package flowrate is suitable considering with discharge elevation (abt. 20m) and adsorption filter and system pressure drop. |  | OFE47862 rev0 OWSAN-5 TEC page 16 pump technical data page 20 pump curve | Detegasa will check and reply. HHI will provide required tie-in pressure or pressure drop at the discharge piping. | HHI provided requested information and waiting for Detegasa response. | Proposal was updated accordingly. | Closed
6 | Process | 2021-07-09 | It was indicated that self prime from dry run up to 3 m meanwhile max. suction elevation is 4.5 in P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1). Bidder to clarify max. suction lift elevation and consider to provide priming provision if required. |  | OFE47862 rev0 OWSAN-5 TEC page 20 pump curve | 3m of dry running is self-priming requirement of pump suction line. Oily water separator and pump suction line to be filled before start-up through fresh water filling line by manual. It will be described in operation manual. | Noted and closed |  | Closed
7 | Process | 2021-07-09 | Bidder to inform any package performance restriction for unit trim condition as per I-RL-3010.1M-1350-960-P4X-009.(or I-RL-3010.2G-1350-960-KES-326) |  | OFE47862 rev0 OWSAN-5 TEC | Detegasa will check and reply comparing with motion value considered in design based on IMO 107. | Detegasa to update on response | 20 -Jul: The package is designed according to MEPC 107(49) requisitions, which highly exceed the design values of the FPSO. Please see the design criteria of MEPC 107(49) Inclination test: Equipment should operate satisfactorily at angles of inclination up to 22.5º in any plane from the normal operating position; | Closed
8 | Process | 2021-07-09 | Bidder to inform the scope of system sizing report.(Vessel,Pump,PSV,CV etc.) |  | OFE47862 rev0 OWSAN-5 TEC | Detegasa will provide vessel calculation only. Others are part of vendor standards design. However, Detegasa will provide datasheets for valves and instruments as part of vendor data. | Noted and closed |  | Closed
9 | Process | 2021-07-09 | Bidder to inform max. operating temperature & design temperature of package(expecially 1st oily water separator) when operating temperature is higher than 60 degC, personnel protection shall be provided as per I-ET-3010.00-1200-431-P4X-001. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1) | Detegasa informed operating temperature set will be 45degC and design temperature will be 60degC except electrical parts in panel. | Noted and closed |  | Closed
10 | Process | 2021-07-09 | Bidder to confirm the requirement of drain nozzel with valve on 1st oily water separator. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1) | Detegasa informed additional drain valve will be considered in pump suction line. It will be included in next proposal. Regarding the comment on drain point for Adsorption separator, "I" in the GAD, Detegasa informed current GAD is preliminary drawing and skid drip pan will be extended to cover drain point. | Noted and closed |  | Closed
11 | Process | 2021-07-09 | Bidder to provide check valve on flush water supply line avoid to contaminate oil water into fresh water line and confirm the requirement of strainer. Purchaser doesn't have check valve and strainer on the line. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1) | HHI requested to include strainer and check valve on flushing fresh water inlet line in Detegasa scope of supply as base scope. Detegasa confirmed and proposal will be updated accordingly. | Noted and closed |  | Closed
12 | Process | 2021-07-09 | Bidder to review set pressure of V22. It seems too narrow between operating pressure and set pressure. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1) | Detegasa will evaluate and reconsider pump and 2nd stage tank sizing. HHI will provide latest pressure drop calculation and layout. Detegasa informed this change will not impact on IMO type approval. | HHI provided requested information and waiting for Detegasa response. | Proposal was updated accordingly. | Closed
13 | Process | 2021-07-09 | Oily Water separator need to ensure vacuum condition. Bidder to confirm. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1) | Detegasa confirms | Noted and closed |  | Closed
14 | Process | 2021-07-09 | Bidder to check pump protection at blockage condition. PSV to be provided at pump downstream. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1) | Detegasa will consider PSV at pump downstream. Proposal will be updated accordingly. | Noted and closed |  | Closed
15 | Process | 2021-07-09 | Purchaser wish to know the purpose of V20. Is it re-circulation required as per IMO MEPC 107(49) 6.1.1? |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ1) | Detegasa confirms that it is recirculation required as per IMO MEPC 107. | Noted and closed |  | Closed
16 | Process | 2021-07-09 | Vendor to advice maximum line size of "L" considering 4.5m max height. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ2) | HHI will provide piping layout. Based on HHI layout information, Detegasa will check and advise. | HHI provided requested information and waiting for Detegasa response. | Proposal was updated accordingly. | Closed
17 | Process | 2021-07-09 | Vendor to advice the function of V2 valve. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ2) | V2 valve is manual recirculation to adjust flow to ensure correct vacuum condition on 1st stage tank. | Noted and closed |  | Closed
18 | Process | 2021-07-09 | Vendor to advice the requirement of heater, RS1 and advice requirment of temperature protection for Heater itselt. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ2) | Heater is to keep the temperature oil on top of 1st stage of tank. In order to remove the oil easily during flashing operation. Electrical heater has thermal temperature switch for electrical heater protection. | Noted and closed |  | Closed
19 | Process | 2021-07-09 | Vendor to advice current line size of G,F is enough to prevent clogging problem of sludge. |  | P&ID_1801-UNIC-44-P-XB-00001_01_Z1 (OWSAN-20423-F01I RZ2) | Detegasa informs that there was no critical problem based on current design. Recommend to keep current line size. | Noted and closed |  | Closed
20 | Mechanical | 2021-07-09 | Interface piping flanges are not matching with project's pining specification, B14H. (FF Vs RF) |  | - | Detegasa confirms on availability on FF flanges based on project requests. | Noted and closed |  | Closed
21 | Mechanical | 2021-07-09 | Bidder to comply with the below instruction for selection of sub vendor list. 1) Super Critical category items within Package Unit Packager(s) shall select the Sub-vendor(s) as pre Appendix I Project Vendor List in Exhibit V - Directives for Procurement. 2) Critical category items within Package Unit Packager(s) shall select the Sub-vendor(s) as pre Appendix I Project Vendor List in Exhibit V - Directives for Procurement. In case Packager wants to present a Sub-Vendor(s) for a critical equipment different(“alternate Sub-Vendor”) from the Appendix I Project Vendor List in Exhibit V, Packager(s) will follow clause 4.7.4 in Exhibit V - Directives for Procurement. 3) For equipment/materials(including bulk materials) NOT covered by the Appendix I Project Vendor List in Exhibit V within Package Unit Packager(s) shall select his own standard Sub-Vendor(s) with proven pre-qualifications for the sub-supplied items. But, Packager(s) shall submit a Pre-Qualification documents for final approval of sub-vendor as requested in section 4.7.3 in Exhibit V. a) A list of similar installations b) Technical capability c) Manufacturing capability d) ISO 9001 certification or equivalent e) Type approval certificates f) Classification Society certificates |  | Exhibit V | 1) Detegasa confirms to follow vendor list for Pressure relief valve. 2) Detegasa proposed own design Oil Monitor, DYNAMIC DOM-107. HHI requested to add this proposed vendor for oil in water analyzer in the deviation list for official approval by Petrobras with detail technical justification. 3) Detegasa shall provide Pre-Qualification documents for items which are not covered in Exhibit V during execution stage, if requested. Detegasa to provide sub supplier list with updating pressure relief valve, 1st/2nd Tanks and information for country. | Detegasa to provide sub supplier list with updating pressure relief valve, 1st/2nd Tanks and information for country. Detegas to update deviation list for oil monitor. | 20 Jul: Deviation for the oil monitor updated in the deviation list | Closed
22 | Mechanical | 2021-07-09 | Bidder to add table shown weight and size for major components in the GA drawing in order to check material handling of those item with Module layout. |  | Bidder's GA Drawing | Detegasa will provide required information in the GA drawing during execution stage after order. | Noted and closed |  | Closed
23 | Mechanical | 2021-07-09 | Bidder to indicate access & maintenance area required volume around skid in the GA drawing. |  | Bidder's GA Drawing | Detegasa will provide required information in the GA drawing during execution stage after order. | Noted and closed |  | Closed
24 | Mechanical | 2021-07-09 | Bidder to confirm and comply on Quality Requirement attached as Appendix 15 in Material Requisition. If there are deviation and/or clarification, it shall be listed and updated in deviation & exception form, Appendix 8 in the MR. Bidder to confirm. |  | Quality Requirement attached as Appendix 15 in Material Requisition. | HHI confirms that Detegasa to consider only documents listed in I-ET-3010.1M-5330-667-P4X-001(SPECIFICATION FOR OILY WATER SEPARATOR PACKAGE (SAO-5330501)). The appendix 15 will be updated accordingly. | Detegas to provide updated deviation list. | Deviation list was updated | Closed
25 | Mechanical | 2021-07-09 | The Project assigned American Bureau of Shipping (ABS) as Classification Society for this project. Bidder shall comply with required ABS rules. The required ABS rules are not limited in Main Package. Bidder shall manage the ABS requirements for sub-equipment /component as well. Bidder shall directly communicate with ABS if required. - Class No. / Hull No.(YY283791/Q554) can be referred for communication with ABS for this project. - Notation ✠A1, Floating Production, Storage and Offloading System (Ship-Type), (S) Buzios Field Santos Basin Brazil, FL(30), 205X, ✠AMCC, EXP, CRC(OC), HAB++(OS), UWILD, HELIDK, OHCM - ABS VEC coordinator: Ms Sirin Safie (Tel: +65 6371 2653, ssafie@eagle.org) - VENDOR / SUB-vendor to allow CS (ABS) to share Vendor Comment List with HHI (Hull Contractor) and his Consortium lead KSL. - VENDOR to enable BUYER oversight access in Eagle Construct (ABS). VENDOR to note that ABS VEC in Singapore can and will direct individual vendors to the nearest design review & survey office. |  | MR | Detegasa confirmed. | Noted and closed |  | Closed
26 | Mechanical | 2021-07-09 | The Operation Manuals shall be delivered in English and Brazilian Portuguese Language including sub order items. |  | MR | Detegasa confirmed. | Noted and closed |  | Closed
27 | Mechanical | 2021-07-09 | Bidder to provide on information of proposed sub vendor for fabrication and assembly. |  | - | Detegasa informed Skid assembly and FAT will be by Detagasa own factory in Spain. | Noted and closed |  | Closed
28 | Mechanical | 2021-07-09 | Bidder shall confirm and comply with allowable nozzle load, Attachment_30-01. |  | - | Detegasa confirmed to follow nozzle load value but any calculation for piping stress is not part of Detegasa scope of work. HHI agreed but confirmed nozzle load values to be indicated in GA drawing during execution stage. | Noted and closed |  | Closed
29 | Mechanical | 2021-07-09 | Bidder to advise boundary of Type Approval for IMO MEPC 107(49). Bidder to advise limitation of compliance project's requirements(especially compliance of all applicable documents in technical specification for oily water separator package(I-ET-3010.1M-5330-667-P4X-001) due to maintain the effect of Type Approval Certificate. |  | MR | Detegasa confirmed to maintain Type Approval for IMO MEPC 107(49). The critical points impact to IMO type approval, if any will be added in deviation list. | Noted and closed |  | Closed
30 | Mechanical | 2021-07-09 | Flange isolation kits shall be provided where applicable as per ANNEX E in I-ET-3010.1M-1200-200-P4X-002_K_HULL PIPING SPECIFICATION. Bidder to confirm. |  | I-ET-3010.1M-1200-200-P4X-002_K_HULL PIPING SPECIFICATION | Detegasa confirmed. | Noted and closed |  | Closed
31 | Mechanical | 2021-07-09 | Structural isolation kits shall be provided where applicable. (e.g. Between Stainless Steel Equipment's Support and Carbon Steel Skid's beam). Bidder to confirm. |  | - | Detegasa confirmed. | Noted and closed |  | Closed
32 | Mechanical | 2021-07-09 | ** Fabrication Site Conditions Supplier shall ensure the suitability of the package or equipment for the fabrication site condition as follows in every respect from design to operation in addition to the offshore site condition: • Location : South Korea • Duration : Maximum 1.5 year • Climate : 4 seasons, 100% relative humidity, Salt laden, marine coastal environment * Ambient temperature : 38.6 deg. C Max. , -16.7 deg. C Min. |  | - | Detegasa recommends to storage the equipment indoor before installation. Detegasa expect that this equipment will not be operated with below 0 deg.C and there is no concern for this clarification point. | Noted and closed |  | Closed
33 | Mechanical | 2021-07-09 | Bidder to check and confirm on the revised Piping Specification For Hull. Refer to attachment #36-1. |  | - | Dedegasa will review Piping Specification for Hull which was provided in this TC No.36. Detegasa will add deviation points in the deviation list, if required. | Noted and closed |  | Closed
34 | Mechanical | 2021-07-09 | - ALL STEEL SERRATED BAR GRATING AND STAIR TREADS SHALL HAVE A MESH 30x100 mm: HEIGHT 30 MM; MINIMUM BEARING BRS THICKNESS 4.76 mm; CROSS BARS DIAMETER 8 mm. GRATING PANELS WITH EDGE BARS WELDED TO BEARING BARS AROUND PERIMETER AND PENETRATIONS; - ALL SERRATED WELDED STEEL GRATING AND STAIR THREADS SHALL BE HOT DIP GALVANIZED BY THE FABRICATOR ACCORDING TO I-ET-3010.00-1200-956-P4X-006 - GENERAL PAINTING; - ALL GRATING PANELS AND STAIR THREADS SHALL BE FASTENED TO SUPPORT STEEL EITHER BY POWER DRIVEN THREADED STUDS OR BY SADDLE CLIPS C/W BOLTS, NUTS, LOCK WASHER. STUDS SHALL USE AISI 316 STAINLESS STEEL. SADDLE CLIPS SHALL BE HOT DIP GALVANIZED. AT LEAST 4 FASTENERS PER SQUARE METER OR PER PIECE. DRAIN HOLES/GUILLIES MAY NOT BE FIXED. STAIR THREADS FASTENED WITH BOLTS AND ITS SURFACE COATING ACCORDING TO BOLT MATERIALS SPECIFICATION GRATING FIXING BY GRATING FABRICATOR; - STEEL GRATING SHALL BE DESIGNED FOR A MINIMUM 5kN/M2 DISTRIBUTED LOAD AND FOR A CONCENTRATED LOAD OF 5kN APPLIED IN 100x100 mm AREA (NOT SIMULTANEOUSLY). STEEL GRATINGS IN AREAS WITH LOADS HIGHER THAN 5kN/M2 SHALL BE RIFIED TO THIS SPECIFIC LOAD CONDITIONS. STAIR THREAD SHALL BE DESIGNED FOR A CONCENTRATED LOAD OF 1.33 kN FOR EACH 600 mm OR FRACTION OF STAIR WIDTH; - MINIMUM GRATING SUPPORTING LENGTH 25 mm, CONSIDER INSTALLATION CLEARANCES TO DETERMINE THIS LENGTH; - MINIIMUM CLEARANCE BETWEEN GRATINGS IS 10 mm; - MEALLIC REMOVABLE FLOOR GRATING SHALL BE EQUALIZED (GROUNDED) TO STRUCTURE POTENTIAL ACCORDING TO REQUIREMENTS OF I-ET-3010.00-5140-700-P4X-001 - SPECIFICATION FOR ELECTRICAL DESIGN FOR OFFSHORE UNITS AND I-DE-3010.00-5140-700-P4X-003 - GROUNDING INSTALLATION TYPICAL DETAILS; - DETAILED DESIGN SHALL ISSUE A REPORT WITH MEASUREMENT OF RESISTANCE BETWEEN REMOVABLE GRATING AND HULL REFERENCE GROUNDING PLATES, ACCORDING TO LIMITS DEFINED BY I-ET-3010.00-5140-700-P4X-001 - SPECIFICATION FOR ELETRICAL DESIGN FOR OFFSHORE UNITS; - GROUNDING OF NON-METALIC FLOOR GRATING IS NOT REQUIRED. |  | - | There are No grating on the skid. In principle, access/maintenance of skid will be from outside(around) skid. | Noted and closed |  | Closed
35 | Mechanical | 2021-07-09 | VENDOR’s standard mechanical completion check sheets are to be detailed for the overall package, as well each individual component (e.g. Pump, Motor, Filters, Instruments, Control panel, etc.) as pre section 8.7 in the MR. The mechanical completion check sheets shall be included in FAT procedure which will be submitted as part of vendor document during execution stage for HHI review and approval. Bidder to confirm. |  | MR | Detegasa will check and revert | Detegasa to update on response | Detegasa confirm. | Closed
36 | Mechanical | 2021-07-09 | Piping flow marking(stripes for identification) shall be provided as per Section 11 in DR-ENGP-I-1.15-R.4_0_COLOR CODING. The details for piping flow marking shall be included in Painting procedure which will be submitted as part of vendor document during execution stage for HHI review and approval. |  | DR-ENGP-I-1.15-R.4_0_COLOR CODING | Detegasa will check and revert | Detegasa to update on response | Detegasa confirm. | Closed
37 | Mechanical | 2021-07-09 | Critical vendor documents which are directly related to HHI’s interface engineering shall be submitted as requested in below. Appendix 5 in MR will be updated accordingly. Bidder to confirm on this submission schedule. 1) Vendor Document Schedule(VDS): LOI + 2 weeks 2) GA Drawing: LOI + 4 weeks (including weight, COG, piping tie-in location, E&I tie-in location, detail of structural interface, table for sub-equipment showing size and weight, required maintenance space around skid and etc.) 3) P&ID: LOI + 4 weeks 4) Utilities Schedule including Elec. Load list : LOI + 4 weeks 5) Single Line Diagrams: LOI + 8 weeks 6) Schematic Diagrams: LOI + 8 weeks |  | Appendix 5 in MR | Detegasa confirmed. | Noted and closed |  | Closed
38 | Mechanical | 2021-07-09 | Bidder to submit utility consumption list including elec. Load list. |  | - | Detegasa will provide updated utility consumption list including elec. Load via separate offer document. | Detegasa to send utility consumption list. | 20-Jul: Noted and confirmed | Closed
39 | Mechanical | 2021-07-09 | Bidder to comply with vendor for oil in water analyser, Advanced Sensor. |  | Exhibit V | Detegasa will add this point in the deviation list. | Noted and closed. Further discussion will be clarified via deviation list. |  | Closed
40 | Mechanical | 2021-07-09 | Bidder to comply with I-ET-3010.1M-5330-667-P4X-001_C_SPECIFICATION FOR OILY WATER SEPARATOR PACKAGE (SAO-5330501) |  | I-ET-3010.1M-5330-667-P4X-001_C_SPECIFICATION FOR OILY WATER SEPARATOR PACKAGE (SAO-5330501) | Detegasa will review and clarify on deviation points, if any via deviation and clarification list. | Noted and closed. Further discussion will be clarified via deviation list. |  | Closed
41 | Automation | 2021-07-09 | Control Narrative and Cause & Effect chart shall be provided as part of vendor data. |  | General | Detegasa does not usually supply this document. We provide a troubleshooting guideline. If it is finally requested, Detegasa can supply that info, but it will have an impact in the price of the package | Noted but Detegasa to provide control/logic description as vendor data. | Detegasa confirm. | Closed
42 | Automation | 2021-07-09 | Test report to include all instrument calibration certification / tubing leak test / instrument mechanical check sheet. |  | General | Detegasa confirms | Noted and closed |  | Closed
43 | Automation | 2021-07-09 | HART type field instrument device shall be applied. |  | GENERAL CRITERIA FOR INSTRUMENTATION PROJECTS(I-ET-3010.00-1200-800-P4X-013) 4.2 Electronic Instrumentation 4.2.1 4 to 20 mA, with addition of digital communication using HART protocol, certified by HART FOUNDATION. | There are no field instruments in our package, consequently, we consider that it is not applicable | Noted and closed |  | Closed
46 | Automation | 2021-07-09 | Package I/O list should be provided. |  | General | To be provided during project execution | Noted and closed |  | Closed
47 | Automation | 2021-07-09 | IP Grade Requirement |  | AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS(I-ET-3010.00-1200-800-P4X-002) 5.1.4 All instruments and their accessories shall be at least IP-56 (IEC 60529) and according to Classification Society rules. 5.11.5 Junction boxes for instrumentation cables in classified or open areas shall have a minimum Ingress Protection rating of IP-56 and shall be "Ex e" or "Ex d" certified and certified for at least Zone 2. 5.13.6.1 Indoor panels and accessories installed in air conditioned room or ventilated room (indoor panels) shall be supplied with IP-22 protection degree, according to IEC 60529, as a minimum. 5.13.7.1 Outdoor panels and accessories shall be supplied with IP-56 protection degree, according to IEC 60529, as a minimum. Hazardous area requirements shall also be taken into account. See also item 4.1. | Detegasa comfirms | Noted and closed |  | Closed
48 | Automation | 2021-07-09 | Junction Boxes Segregation Requirement |  | According to AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS(I-ET-3010.00-1200-800-P4X-002) 5.11.4 Signals to CSS related to PCS, PSD, HCS, HSD and FGS sub-systems, must be segregated in different terminal strips and multicables (where applicable), when installed inside the same junction box. The junction boxes shall be segregated into 3 types: • TYPE 1: for signals using flame-resistant cables (PSD/HSD/FGS); • TYPE 2: for signals related to safety interlocks (PSD/HSD); • TYPE 3: for signals related to process control (PCS/HCS). | No junction boxes in our scope of supply | Noted and closed |  | Closed
49 | Automation | 2021-07-09 | Enclosure Material Requirment |  | According to GENERAL CRITERIA FOR INSTRUMENTATION PROJECTS(I-ET-3010.00-1200-800-P4X-013) 6.3.2, Boxes or enclosures of electronic field instruments shall be made of ASTM A351 Gr. CF8M stainless steel. | No field instruments in our package | Noted and closed |  | Closed
50 | Automation | 2021-07-09 | According to P1 package catagory requirements, package system shall consist and set the function. |  | AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS(I-ET-3010.00-1200-800-P4X-002) 4. PACKAGE INSTRUMENTATION AND CONTROL | Noted | Noted and closed |  | Closed
51 | Automation | 2021-07-09 | Control Panel Color Requirement |  | COLOR CODING (DR-ENGP-I-1.15-R.4) 17.2. Control Panels [RC]: Light Cream (MUNSELL notation 2.5 Y 9/4). | Detegasa confirms | Noted and closed |  | Closed
52 | Automation | 2021-07-09 | Instrument Color Requirement |  | COLOR CODING (DR-ENGP-I-1.15-R.4) 17.1. Instruments: follow the piping or equipment color. * See note bellow. Instrumentos: * Note: For new parts, it may be kept the original maker painting, except for control valves. GENERAL PAINTING(I-ET-3010.00-1200-956-P4X-002) | Detegasa confims | Noted and closed |  | Closed
53 | Automation | 2021-07-09 | Redundant power for package shall be provided. |  | Redundant power for package shall be provided. | To be discussed | HHI will more detail for this request. The available power supplied by the Vendor to be used by the Automation panels is defined in I-ET-3010.00-5140-700-P4X-003 – ELECTRICAL REQUIREMENTS FOR PACKAGES FOR OFFSHORE UNITS. It is part of the panel SUPPLIER’s scope to convert and redundantly distribute the different power supplies inside panels, including, where necessary, redundant AC/DC or DC/DC stabilized power supply units for cabinet’s internal distribution of 24 VDC. (22-July) As mentioned in Annex 1 of I-ET-3010.00-5140-700-P4X-003, 1 feeder of 220V(1ph) will be supplied to OWS control panel by HHI. Bidder shall install 2 sets of AC/DC stabilized power supply units for cabinets’ internal distribution of 24VDC as mentioned in I-ET-3010.00-5520-888-P4X-001, para 6.4. (26-July) With regard to power supplies, it’s confirmed that “440/480V 60Hz 3ph”, 220V 1ph CC(control), 220V 1ph AC(space heater for control panel) will be provided. Bidder to install 2 sets of AC/DC stabilized power supply units for control. Motor space heater is not requirement. | 20 -Jul: The package will be fed by one main power supply to the main control system (440 V 60 Hz 3 Ph) and one auxiliary electrical supply for the space heater of the cabinet. Electrical istribution and step down by means of transformers will be carried out internally in the package. in that sense we do not really understand the requisition about power redundancy, more precisely, redundant distribution of power supplies. Please clarify further this point (22-July): We understand that our package will be fed by three independent power supplies: - 440/480 V 60 Hz 3 Ph - 220 V 1 Ph CC (control) - 220 V 1 Ph AC (space heater for main control panel) * We understand that space heater is NOT required for the motor of the pump (26-July): Noted and confirmed | Closed
54 | Automation | 2021-07-09 | SPARE PARTS: |  | According to AUTOMATION, CONTROL AND INSTRUMENTATION ON PACKAGE UNITS(I-ET-3010.00-1200-800-P4X-002) 5.1.5 Continuity of spare parts supply and maintenance shall be given for a 5 year period for instrument. | Detegasa confirms | Noted and closed |  | Closed
55 | Automation | 2021-07-09 | Cable Tray Material Requirement |  | GENERAL CRITERIA FOR INSTRUMENTATION PROJECTS(I-ET-3010.00-1200-800-P4X-013) 17.4.1 Cable trays shall be made of AISI 316 stainless steel. Cable trays made of galvanized steel may be used in sheltered areas (rooms, etc.). | Detegasa comfirms | Noted and closed |  | Closed
56 | Automation | 2021-07-09 | Cable tray also shall be segregated by signal type. |  | General | Detegasa confirms | Noted and closed |  | Closed
57 | Automation | 2021-07-09 | Instruments in type P1 packages are not directly and permanently connected to AMS(Asset Management System), although the DTM/DD of package instruments for P1 Packages shall be delievered and configured in AMS, as defined in I-MD-3010.1M-1200-800-P4X-001_D, in this way, allowing the handheld use for these instruments. As stated in I-MD-3010.1M-1200-940-P4X-025, a descriptive memorandum (MD) has precedence over a technical specification (ET), so the clause 9.14.4.11 of I-MD-3010.1M-1200-800-P4X-001_D shall be complied. |  | I-MD-3010.1M-1200-800-P4X-001 I-MD-3010.1M-1200-940-P4X-025 | To be discussed | HHI will more detail for this request. Hart protocol type of instruments for deliverying DTM/DD to be provided. | 20- Jul: Noted and confimed if instruments provide signals to AMS. If those signals are only for internal use in the package, HART protocol will not be considered | Closed
58 | Automation | 2021-07-09 | PLC and HMI shall be selected from below list. 1) GE 2) SIEMENS 3) Rockwell Because Standardization for PLC and HMI is requested in P-78 Project. Final selection of supplier for PLC and HMI will be informed during Execution Stage. |  | - | Our scope includes a SIEMENS PLC. In case of changes, it might have an impact in the price | Noted and closed. HMI also to be included in base scope as per response on TC#45. |  | Closed
59 | Electrical | 2021-07-09 | Bidder's Technical Specification 5.2 Electrical and control design basis The equipment includes a main control panel to be installed in safe zone, which contains the motor starters and the main power connection. |  | Motor starters will be provided by Buyer. Control panel only shall be provided by Bidder. Interface cable between Motor starters and control panel shall be provided by Buyer. | The electrical connection between the starter and the motor is within the limits of our package | Noted. Further clarification shall be done during detail design if required. |  | Closed
60 | Electrical | 2021-07-09 | Oily Water Separator General Arrangement Electrical Supply : 690Vac, 3ph, 60Hz |  | Motor shall be 440Vac, 3ph, 60Hz. | Detegasa confirms | Noted. |  | Closed
61 | Electrical | 2021-07-09 | It shall be considered a design ambient temperature of 45°C, continuously. Classification Society requirements, when more restrictive, shall be complied with. Induction motors shall have rated power calculated, with service factor 1.0, considering the following oversizing factors applied to driven machine rated brake power: a) 25% for motors with rated power lower than 22kW; |  | - |  |  | Detegasa confirm. | Closed
62 | Electrical | 2021-07-09 | When cables are subjected to mechanical impacts, proper additional protection by covers shall be foreseen. Cable trays covers shall be of the same material and the same thickness of cable trays they are protecting. Bidder to confirm. |  | I-ET-3010.00-5140-700-P4X-002_E_SPEC FOR ELEC MATERIAL AND EQ FOR OFFSHORE UNITS | Detegasa confirms | Noted. |  | Closed
63 | Process | 2021-07-13 | Bidder to clarify on scope for V29. |  | Bidder's P&ID | V29 is NOT part of Detegasa scope. HHI confirms V29 is part of HHI scope. | Noted. |  | Closed
64 | Mechanical | 2021-07-22 | Bidder shall perform the initial thickness measurement on all equipment and piping under NR-13 and SPIE. The Ultrasonic method shall be applied. The specific points on the main parts of equipment and piping where ultrasonic measurements will be identified and communicated during execution stage. In general, the scope of SPIE includes following items as minimum but specific points will be fixed during execution stage: 1) Pressure vessels and piping covered by item 13.2.1 of NR-13. 2) Pressure vessels and piping NOT covered by item 13.2.1 of NR-13. 3) Other equipment, like non-metallic vessels, tanks, pig launcher/receiver, PSV, plate heat exchangers and so on. For example, piping containing compressed air (class C as per NR-13), water (class D as per NR-13) is included in the scope of thickness measurement. |  | - |  | (19-Aug) Noted. | 22 -July: Noted and confirmed, we will take it into consideration for the revision of the quotation 19-August:Please note that Detegasa has not a SPIE. Thickness measurements using UT shall be carried by an external Detegasa supplier and technicians qualified as level 2 according ISO 9712. Thickness measurements shall be carried out on the points of the tanks and piping required by HHI. | Closed

## Sheet1 (hidden)
8.6
8.7
8.8 |  | Painting
Protective Coating & Linning
8.9
8.1
By Vendor
9
10 |  | Shop Inspection & Test
- Inspection and test at shop for equipment
- Inspection ans test at shop for Instrument, including
function test at shop
11.0 |  | Documentation :
|  | Documents + Drawing submission |  |  |  |  | As per VDRL of Doc. BRA- RQ- M-004
Rev Q1
12.0 | SKID MODULE SIZE AND WEIGHT
Glycol Regeneration Skid
- Size
|  |  |  | First Level | 12m x 6 m
|  |  |  | Second Level | 6m x 6m
|  |  |  | Total Height | 9 m
|  |  |  | - Weight | By Vendor
13 | SITE SUPERVISION |  |  |  | Required
14 | TRAINING |  |  |  | Required
15 | ACCEPTANCE CRITERIA |  |  |  | As per Cl. 6.8. Of Doc
BRA- RQ-M-004 Rev Q1